## Site
Site
Weather Data
Brussels | energyplus.net/weather
Design Days
Summer DD | BRUSSELS Ann Clg .4% Condns DB=>MWB
Winter DD | BRUSSELS Ann Htg 99.6% Condns DB
References
ASHRAE 2009. Handbook of Fundamental, Chapter 14
> Which DD should we use?
Annual Heating and Humidification Design Conditions "The month with the lowest mean dry-bulb temperature is used, for example, to determine the time of year where the maximum heating load occurs. The 99.6 and 99.0% design conditions are often used in sizing heating equipment." Annual Cooling, Dehumidification, and Enthalpy Design Conditions. "[...] The 0.4, 1.0, and 2.0% dry-bulb temperatures and mean coincident wet-bulb temperatures often represent conditions on hot, mostly sunny days. These are often used in sizing cooling equipment such as chillers or air-conditioning units."
Cooling
DB=>MWB | Chillers and air conditionners
Condns WB=> MDB | Cooling Towers and other evaporative coolers
DP=>MDB | useful for humidity control applications, i.e. desiccant cooling and dehumidification, cooling-based dehumidification, and fresh-air ventilation systems
Condns Enth=>MDB | this is used for calculating cooling loads caused by infiltration and/or ventilation into buildings. Enthalpy represents the total heat content of air (the sum of its sensible and latent energies)
Heating
Condns DB | General heating applications
Condns DP=>MCDB | to size equipment for humidification applications.
Condns WS=>MCDB | Wind design data provide information for estimating peak loads accounting for infiltration
2013 Annual Design Conditions Definitions for all ASHRAE Design Condition Locations:
http://energyplus.helpserve.com/knowledgebase/article/View/129/47/design-conditions-definitions-annual-for-all-ashrae-2013-design-condition-locations

## Schedules
Schedules
Spaces | Type | References | Remarks | Units | Period | 0-1 | 1-2 | 2-3 | 3-4 | 4-5 | 5-6 | 6-7 | 7-8 | 8-9 | 9-10 | 10-11 | 11-12 | 12-13 | 13-14 | 14-15 | 15-16 | 16-17 | 17-18 | 18-19 | 19-20 | 20-21 | 21-22 | 22-23 | 23-24
Offices
| Equipments / Full | From DOE Prototype Buildings | - | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Equipments / 75% | From DOE Prototype Buildings | We consider that the relation btw occupancy/equipement is not linear. A 75% occupancy does not equal a 75% equipment use. Hyp: 80% | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Lights | ASHRAE Schedules, From DOE Prototype Buildings (decrease at the end slightly postponed, 1 hour, 6pm instead of 5 pm) | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.3 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.45 | 0.3 | 0.3 | 0.2 | 0.1 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Occupancy / Full | ASHRAE Schedules, adapted according to Obyn et al. | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Occupancy / 75% | ASHRAE Schedules, adapted according to Obyn et al. | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.7 | 0.7 | 0.7 | 0.7 | 0.35 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | ASHRAE Schedules, revised. Temperature values: ISO13790, 2008 in Obyn et al. | Temperature values change based on the sensitivity analysis. | °C | weekdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16
[5 empty] | Saturdays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16
[5 empty] | Sundays/holidays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
| Cooling | ASHRAE Schedules, revised. Temperature values: ISO13790, 2008 in Obyn et al. | Temperature values change based on the sensitivity analysis. | °C | weekdays | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 29 | 29
[5 empty] | Saturdays | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 29 | 29 | 29 | 29 | 29 | 29
[5 empty] | Sundays/holidays | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
| People activity | Obyn et al. | total heat (adapted men/women) for seated, very light work | W | Default | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
Hall and corridors
| Lights | ASHRAE Schedules | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.5 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.8 | 0.6 | 0.3 | 0.1 | 0.05 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Elevators | From Commercial Building Energy Saver (CBES) Prototype Models: cbes.lbl.gov | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0.7 | 0.45 | 0.4 | 0.45 | 0.6 | 0.5 | 0.4 | 0.4 | 0.5 | 0.6 | 0.2 | 0.1 | 0.05 | 0.05 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15 | 0.15 | 0.2 | 0.2 | 0.25 | 0.2 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Equipments | From DOE Prototype Buildings | - | - | weekdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.85 | 0.85 | 0.85 | 0.85 | 0.75 | 0.85 | 0.85 | 0.85 | 0.85 | 0.5 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Saturdays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.4 | 0.5 | 0.5 | 0.5 | 0.5 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
[5 empty] | Sundays/holidays | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| People activity | Obyn et al. | total heat (adapted men/women) for slow walking or standing activity | W | Default | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
| Occupancy | See offices | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.95 | 0.95 | 0.95 | 0.95 | 0.5 | 0.95 | 0.95 | 0.95 | 0.95 | 0.7 | 0.4 | 0.4 | 0.1 | 0.1 | 0.05 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
| Heating | ASHRAE Schedules, revised | - | °C | weekdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16
[5 empty] | Saturdays | 16 | 16 | 16 | 16 | 16 | 16 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 16
[5 empty] | Sundays/holidays | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Data center
| Equipments | ASHRAE Schedules | - | - | weekdays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
[5 empty] | Saturdays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
[5 empty] | Sundays/holidays | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75
| Lights | ASHRAE Schedules | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HVAC | - | - |  | Default | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Heating | - | - | °C | weekdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Saturdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Sundays/holidays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
| Cooling | - | - | °C | weekdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Saturdays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
[5 empty] | Sundays/holidays | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 27
Basement
| Lights | - | - | - | weekdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.25 | 0.25 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.25 | 0.25 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Saturdays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
[5 empty] | Sundays/holidays | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| Occupancy | - | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.15 | 0.7 | 0.7 | 0.7 | 0.7 | 0.35 | 0.7 | 0.7 | 0.7 | 0.7 | 0.5 | 0.3 | 0.3 | 0.1 | 0.1 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HVAC | ASHRAE Schedules | - | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  | ASHRAE Schedules |  |  | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  | ASHRAE Schedules |  |  | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Infiltration
| Infill Quarter On | ASHRAE Schedules | when system on, the infiltration is reduced to 0.25 of the full value because assume that when the system is on, the building is pressurized. When system off, assume that infiltration can move freely into the building. According to the National Institute of Standards and Technology (US), this isn't necessarily the case. They created this OS measure: https://bcl.nrel.gov/node/83101 | - | weekdays | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1
|  | ASHRAE Schedules |  |  | Saturdays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 1 | 1 | 1 | 1 | 1 | 1
|  | ASHRAE Schedules |  |  | Sundays/holidays | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HVAC
| Chilled Water Temperature |  | "=44F, From AHRI standard test conditions, 44F Leaving water temperature (LWT), and 54F for EWT. For water cooling tower, Wet bulb temperature of outside air (EAT wb) (in standard conditions)= 78F; LWT: 85F; EWT: 95. i.e., range of 10F and an approach of 7F. This means a design to come close to 7F of this value. That gives 85F of chilled water temperature coming out. See: 2018 Standard for Performance Rating of Water-chilling and Heat Pump Water-heating Packages Using the Vapor Compression Cycle. http://www.ahrinet.org/App_Content/ahri/files/STANDARDS/AHRI/AHRI_Standard_551-591_SI_2018.pdf | °C | default | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
| Deck Temperature |  | Space temp =75F, deck =spacetemp - 20F = 55F > 24°C et 13°C. Idem pour l'hiver, même SAT car des locaux ont besoin de cooling même en hiver, le reste faisant (beaucoup trop) de reheat. VAV with reheat systems are usually controlled at the central air handling unit to a cool deck temperature (usually 55F),. supply air temperature; default value is 20F below space temperature for cooling (usually set at 75°F, 24°C) | °C | default | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
| Deck Temperature |  | Space temp =75F, deck =spacetemp - 20F = 55F > 24°C et 13°C. Idem pour l'hiver, même SAT car des locaux ont besoin de cooling même en hiver, le reste faisant (beaucoup trop) de reheat. VAV with reheat systems are usually controlled at the central air handling unit to a cool deck temperature (usually 55F),. supply air temperature; default value is 20F below space temperature for cooling (usually set at 75°F, 24°C) | °C | default | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
| HVAC |  |  | - | weekdays | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
[5 empty] | Saturdays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | Sundays/holidays | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Construction
Construction
Roof
| _Roof | Built-up roofing | Roof insulation | Concrete floor, 200mm
Walls
structural wall, int | _Gypsum13_Concrete200mm_Gypsum13 | Gypsum 13mm | Concrete, 200mm | Gypsum 13mm
Floor and ceiling
Intermediate slab | _ConcreteAndCarpet | Carpet pad | Concrete, 200mm
ground contact surfaces, basement | _Concrete_300mm | Concrete, 300mm
Plenum | _DropCeiling | Ceiling
Materials
Thermal Curtain only | Brand | Isotiss | -
| Solar transmittance | 0.12 | -
| Solar reflectance | 0.71 | -
| Visible transmittance | 0.12 | -
| Visible Reflectance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0.05 | -
| Thickness | 0.01 | m
| Conductivity | 0.046 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
Thermal Curtain w/ air wall | Brand | Isotiss | -
| Solar transmittance | 0.12 | -
| Solar reflectance | 0.71 | -
| Visible transmittance | 0.12 | -
| Visible Reflectance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0.05 | -
| Thickness | 0.13 | m
| Conductivity | 0.28261 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
Frame, low efficiency | Brand | Generic | -
| Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 5.5 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, high efficiency | Brand | Wicona, Wictec 50 | -
| Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 1.2 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, low efficiency w/ thermal curtain | Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 1.5581 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Frame, high efficiency w/ thermal curtain | Width | 0.1 | m
| Outside projection | 0.024 | m
| Insode projection | 0.12 | m
| Conductance | 0.7732 | W/m².K
| Ratio of frame-edge glass conductance to center-of-glass conductance | 1 | -
| Solar absorptance | 0.7 | -
| Visible absorptance | 0.7 | -
| Thermal hemispherical emissivity | 0.9 | -
Exterior shading | Brand | https://verosol.com/product/enviroscreen-g3-optimum/
| Solar transmittance | 0.05 | -
| Solar reflectance | 0.74 | -
| Visible transmittance | 0.04 | -
| Visible Reflectance | 0.9 | -
| Thermal hemispherical emissivity | 0.9 | -
| Thermal transmittance | 0 | -
| Thickness | 0.0005 | m
| Conductivity | 0.15 | W/m.K
| Shade to glass distance | 0.05 | m
| Airflow permeability | 0.1 | -
| Emissivity front | 0.68 | -
| Emissivity back | 0.282 | -
| TIR | 0.149 | -
| Permeability factor | 0.111 | -
_Spandrel_Equivalent | Thickness | 0.205 | m
Equivalent to: 1 layer of safety glass, 8mm; 50mm of air cavity; 120mm of XPS insulation | Conductivity | 0.081 | W/m.K
| Density | 536 | kg/m³
| Specific heat | 1085 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
_Wall_Concrete300mm | Thickness | 0.3 | m
| Conductivity | 1.4
| Density | 2100 | kg/m³
| Specific heat | 840 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Carpet pad | Thermal resistance | 0.22 | m².K/W
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Roof insulation | Thermal resistance | 5.31 | m².K/W
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Gypsum_13mm | Thickness | 0.0127 | m
| Conductivity | 0.16 | W/m.K
| Density | 800 | kg/m³
| Specific heat | 1090 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.5 | -
_Ceiling | Thickness | 0.02 | m
| Conductivity | 0.057 | W/m.K
| Density | 288 | kg/m³
| Specific heat | 1339 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.5 | -
_Floor_Concrete200mm | Thickness | 0.2 | m
| Conductivity | 1.4 | W/m.K
| Density | 2100 | kg/m³
| Specific heat | 840 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Std Wood | Thickness | 0.15 | m
| Conductivity | 0.12 | W/m.K
| Density | 540 | kg/m³
| Specific heat | 1210 | J/kg.K
| Thermal Absorptance | 0.9 | -
| Solar Absorptance | 0.7 | -
| Visible Absorptance | 0.7 | -
Bronze Glass_6mm | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.486 | -
| Front side solar reflectance | 0.053 | -
| Back side solar reflectance | 0.053 | -
| Visible Transmittance | 0.533 | -
| Front side visible reflectance | 0.056 | -
| Back side visible reflectance | 0.056 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
Clear_55.2 | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.7 | -
| Front side solar reflectance | 0.066 | -
| Back side solar reflectance | 0.066 | -
| Visible Transmittance | 0.868 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.078 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.791 | W/m.K
Clear_55.2_HighLT_HighSHGC | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.753 | -
| Front side solar reflectance | 0.069 | -
| Back side solar reflectance | 0.069 | -
| Visible Transmittance | 0.879 | -
| Front side visible reflectance | 0.079 | -
| Back side visible reflectance | 0.079 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.787 | W/m.K
Clear 6mm | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.809 | -
| Front side solar reflectance | 0.072 | -
| Back side solar reflectance | 0.072 | -
| Visible Transmittance | 0.888 | -
| Front side visible reflectance | 0.079 | -
| Back side visible reflectance | 0.079 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
Clear_6mm_HighLT | Thickness | 0.006 | m
Calculated with Window 7.7 software | Solar transmittance | 0.353 | -
| Front side solar reflectance | 0.375 | -
| Back side solar reflectance | 0.494 | -
| Visible Transmittance | 0.787 | -
| Front side visible reflectance | 0.081 | -
| Back side visible reflectance | 0.077 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.841 | -
| Conductivity | 1 | W/m.K
Clear 8mm | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.777 | -
| Front side solar reflectance | 0.07 | -
| Back side solar reflectance | 0.07 | -
| Visible Transmittance | 0.878 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.078 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 1 | W/m.K
LowE_55.2_HighLT | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.464 | -
| Front side solar reflectance | 0.394 | -
| Back side solar reflectance | 0.255 | -
| Visible Transmittance | 0.82 | -
| Front side visible reflectance | 0.084 | -
| Back side visible reflectance | 0.102 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.03 | -
| Back side infrared emissivity | 0.841 | -
| Conductivity | 0.787 | W/m.K
LowE_55.2_LowLT_LowSHGC | Thickness | 0.0105 | m
Calculated with Window 7.7 software | Solar transmittance | 0.464 | -
| Front side solar reflectance | 0.082 | -
| Back side solar reflectance | 0.089 | -
| Visible Transmittance | 0.679 | -
| Front side visible reflectance | 0.078 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.84 | -
| Conductivity | 0.865 | W/m.K
SC_8mm_HighLT_HighSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.353 | -
| Front side solar reflectance | 0.375 | -
| Back side solar reflectance | 0.494 | -
| Visible Transmittance | 0.787 | -
| Front side visible reflectance | 0.081 | -
| Back side visible reflectance | 0.077 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.031 | -
| Conductivity | 1 | W/m.K
SC_8mm_LowLT_LowSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.27 | -
| Front side solar reflectance | 0.314 | -
| Back side solar reflectance | 0.5 | -
| Visible Transmittance | 0.539 | -
| Front side visible reflectance | 0.147 | -
| Back side visible reflectance | 0.163 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.028 | -
| Conductivity | 1 | W/m.K
SC_8mm_LowLT_VeryLowSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.187 | -
| Front side solar reflectance | 0.38 | -
| Back side solar reflectance | 0.619 | -
| Visible Transmittance | 0.386 | -
| Front side visible reflectance | 0.297 | -
| Back side visible reflectance | 0.313 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.84 | -
| Back side infrared emissivity | 0.028 | -
| Conductivity | 1 | W/m.K
SC_8mm_midLT_midSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.243 | -
| Front side solar reflectance | 0.365 | -
| Back side solar reflectance | 0.489 | -
| Visible Transmittance | 0.557 | -
| Front side visible reflectance | 0.116 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.025 | -
| Conductivity | 1 | W/m.K
SC_8mm_midLT_midSHGC | Thickness | 0.008 | m
Calculated with Window 7.7 software | Solar transmittance | 0.243 | -
| Front side solar reflectance | 0.365 | -
| Back side solar reflectance | 0.489 | -
| Visible Transmittance | 0.557 | -
| Front side visible reflectance | 0.116 | -
| Back side visible reflectance | 0.075 | -
| Infrared transmittance | 0 | -
| Front side infrared emissivity | 0.841 | -
| Back side infrared emissivity | 0.025 | -
| Conductivity | 1 | W/m.K

## Construction_igus
| Construction, glazing | [9 empty] | Data Window7.7
[15 empty] | U-Factor | SHGC | VT |  |  |  | Data Window7.7
| Name part 1 | Layers |  |  | U-Factor | SHGC | VT | Name part 2 | Name part 3 |  |  | 1 | 2 | 3 | W/m².K | - | -
# |  | #1 | #2 | #3 | W/m².K | - | - |  |  | ref | DG_8-10-55.2_bronze | Planibel Bronze | Stratobel Clearlite | - | 2.706 | 0.464 | 0.364 |  |  |  |  | Tsol | Rsol | Tvis
| Single Glazing | [19 empty] | 55.2
sg_1 | SG_55.2_clear | Stratobel Clearlite | - | - | 5.57 | 0.808 | 0.879 | - | - | 1 | DG_8-10-55.2_clear | Clear | Stratobel Clearlite | - | 2.706 | 0.692 | 0.768 |  |  | 4509 | Stratobel Clearlite | 0.753 | 0.069 | 0.879
sg_2 | SG_¦55.2_clear | Stratobel iplus Top 1.0 | - | - | 3.099 | 0.445 | 0.745 | - | - | [10 empty] | 4430 | Stratobel Low-e Top N+ | 0.492 | 0.18 | 0.84
[10 empty] | 1 | SG_55.2_clear | Stratobel Clearlite | - | - | 5.57 | 0.808 | 0.879 |  |  | 4253 | Stratobel iplus Top 1.0 | 0.391 | 0.274 | 0.745
| Double Glazing Old | [8 empty] | 2 | SG_¦55.2_clear | Stratobel iplus Top 1.0 | - | - | 3.099 | 0.445 | 0.745
dg_init | DG_8-10-55.2_bronze | Planibel Bronze | Stratobel Clearlite | - | 2.706 | 0.464 | 0.364 | - | - | [11 empty] | 8mm
dg_0 | DG_8-10-55.2_clear | Clear | Stratobel Clearlite | - | 2.706 | 0.692 | 0.768 | - | - | 1 | DG_8-18Arg-55.2_clear | Clearvision | Stratobel Clearlite | - | 2.51 | 0.785 | 0.806 |  |  | 891 | Clear | 0.761 | 0.067 | 0.869
[10 empty] | 2 | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | - | 1.435 | 0.592 | 0.768 | highSHG_highLT |  | 4336 | Clearvision | 0.892 | 0.078 | 0.911
| Double Glazing High Efficiency | [8 empty] | 3 | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel iplus Top 1.0 | - | 1.419 | 0.481 | 0.687 |  |  | 4370 | Planibel top Nplus | 0.572 | 0.284 | 0.86
dg_1 | DG_8¦-18Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | - | 1.903 | 0.492 | 0.593 | midSHG_midLT | - | 4 | DG_8¦-18Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | - | 1.45 | 0.539 | 0.76 | midSHG_highLT |  | 4446 | Stopray Vision-36T | 0.187 | 0.619 | 0.386
dg_2 | DG_8¦-18Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | - | 1.45 | 0.539 | 0.76 | midSHG_highLT | - | 5 | DG_8¦-18Arg-¦55.2_ | Planibel top Nplus | Stratobel Low-e Top N+ | - | 1.404 | 0.482 | 0.725 |  |  | 4211 | Sunergy Clear | 0.498 | 0.104 | 0.669
dg_3 | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | - | 1.435 | 0.592 | 0.768 | highSHG_highLT | - | 6 | DG_8¦-18Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | - | 1.398 | 0.408 | 0.647 |  |  | 4239 | Stopsol Classic Clear | 0.473 | 0.277 | 0.374
dg_4 | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 1.43 | 0.341 | 0.696 | lowSHG_highLT | - | 7 | DG_8¦-18Arg-55.2_ | Stopray Vision-36T | Stratobel Clearlite | - | 1.424 | 0.203 | 0.348 |  |  | 4478 | Stopray Vision-72 | 0.353 | 0.494 | 0.787
dg_5 | DG_8¦-18Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | - | 1.405 | 0.248 | 0.493 | lowSHG_midLT | - | 8 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel Low-e Top N+ | - | 1.397 | 0.198 | 0.33 |  |  | 4469 | Stopray Vision-51T | 0.243 | 0.489 | 0.557
dg_6 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | - | 1.393 | 0.183 | 0.302 | lowSHG_lowLT | - | 9 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | - | 1.393 | 0.183 | 0.302 | lowSHG_lowLT
[10 empty] | 10 | DG_8¦-18Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | - | 1.405 | 0.248 | 0.493 | lowSHG_midLT |  |  | 6mm
| Triple Glazing | [8 empty] | 11 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | - | 1.39 | 0.244 | 0.47 |  |  | 4340 | Planibel Clearvision | 0.637 | 0.118 | 0.789
tg_1 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | Planibel Clearvision | 1.037 | 0.318 | 0.643 | lowSHG_highLT | - | 12 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel iplus Top 1.0 | - | 1.387 | 0.22 | 0.421
tg_2 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | Planibel Clearvision | 1.022 | 0.229 | 0.455 | lowSHG_midLT | - | 13 | DG_8¦-18Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | - | 1.903 | 0.492 | 0.593 | midSHG_midLT |  |  | 8mm, bronze
tg_3 | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | Planibel Clearvision | 0.98 | 0.554 | 0.709 | highSHG_highLT | - | 14 | DG_8¦-18Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | - | 1.43 | 0.403 | 0.565 |  |  | 4456 | Sunlux Orion Bronze | 0.179 | 0.13 | 0.18
tg_4 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.828 | 0.374 | 0.523 | midSHG_midLT | - | 15 | DG_8¦-18Arg-¦55.2_ | Sunergy Clear | Stratobel iplus Top 1.0 | - | 1.416 | 0.341 | 0.507 |  |  | 4268 | Planibel Bronze | 0.431 | 0.051 | 0.413
tg_5 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.682 | 0.386 | 0.6 | midSHG_highLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
tg_6 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.674 | 0.164 | 0.284 | lowSHG_lowLT | - | 17 | DG_8¦-18Arg-¦55.2_ | Stopsol Classic Clear | Stratobel Low-e Top N+ | - | 1.435 | 0.31 | 0.32
| Triple Glazing, w/ krypton and xenon | [8 empty] | 11 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | - | 1.39 | 0.244 | 0.47 |  |  | 4340 | Planibel Clearvision | 0.637 | 0.118 | 0.789
tg_5k | TG_8¦-14krypton-6-14krypton-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.6 | 0.386 | 0.6 | midSHG_highLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
tg_5x | TG_8¦-14xenon-6-14xenon-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.5 | 0.386 | 0.6 | midSHG_highLT | - | 16 | DG_8¦-18Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | - | 2.508 | 0.468 | 0.338 |  |  | 116 | Generic Bronze Glass | 0.387 | 0.05 | 0.433
[10 empty] | 18 | DG_8¦-18Arg-¦55.2_ | Stopsol Classic Clear | Stratobel iplus Top 1.0 | - | 1.419 | 0.256 | 0.293
| Smart Glazing | [8 empty] | 19 | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 1.43 | 0.341 | 0.696 | lowSHG_highLT
sgA0 | Sage Glass, Saint Gobain | [8 empty] | 20 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | - | 1.399 | 0.335 | 0.664
[10 empty] | 21 | DG_8¦-18Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | - | 1.394 | 0.3 | 0.594
[10 empty] | 1 | TG_8-14Arg-6-14Arg-55.2_clear | Clearvision | Stratobel Clearlite | Planibel Clearvision | 1.575 | 0.738 | 0.745
[10 empty] | 2 | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | Planibel Clearvision | 0.98 | 0.554 | 0.709 | highSHG_highLT
[10 empty] | 3 | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.97 | 0.455 | 0.638
[10 empty] | 4 | TG_8¦-14Arg-6-14Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | Planibel Clearvision | 1.048 | 0.503 | 0.701
[10 empty] | 5 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel Low-e Top N+ | Planibel Clearvision | 0.689 | 0.451 | 0.668
[10 empty] | 6 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.682 | 0.386 | 0.6 | midSHG_highLT
[10 empty] | 7 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-36T | Stratobel Clearlite | Planibel Clearvision | 1.033 | 0.188 | 0.327
[10 empty] | 8 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel Low-e Top N+ | Planibel Clearvision | 0.681 | 0.178 | 0.31
[10 empty] | 9 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.674 | 0.164 | 0.284 | lowSHG_lowLT
[10 empty] | 10 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | Planibel Clearvision | 1.022 | 0.229 | 0.455 | lowSHG_midLT
[10 empty] | 11 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-51T | Stratobel Low-e Top N+ | Planibel Clearvision | 0.674 | 0.22 | 0.434
[10 empty] | 12 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-51T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.667 | 0.199 | 0.39
[10 empty] | 13 | TG_8¦-14Arg-6-14Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | Planibel Clearvision | 1.293 | 0.453 | 0.549
[10 empty] | 14 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.828 | 0.374 | 0.523 | midSHG_midLT
[10 empty] | 15 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.819 | 0.318 | 0.471
[10 empty] | 16 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopsol Classic Clear | Stratobel Clearlite | Planibel Clearvision | 1.574 | 0.434 | 0.318
[10 empty] | 17 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopsol Classic Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.979 | 0.293 | 0.301
[10 empty] | 18 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopsol Classic Clear | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.969 | 0.244 | 0.276
[10 empty] | 19 | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | Planibel Clearvision | 1.037 | 0.318 | 0.643 | lowSHG_highLT
[10 empty] | 20 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-72 | Stratobel Low-e Top N+ | Planibel Clearvision | 0.822 | 0.303 | 0.614
[10 empty] | 21 | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-72 | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.819 | 0.275 | 0.553
Single Glazing w/ thermal curtain
[10 empty] | 1AT | SG_55.2_clear | Stratobel Clearlite | - | - | 1.5636 | 0.808 | 0.879 | - | _TC
[10 empty] | 1BT | SG_¦55.2_clear | Stratobel iplus Top 1.0 | - | - | 1.2777 | 0.445 | 0.745 | - | _TC
Double Glazing Old w/ thermal curtain
[10 empty] | 0AT | DG_8-10-55.2_bronze | Planibel Bronze | Stratobel Clearlite | - | 1.2055 | 0.464 | 0.364 | - | _TC
[10 empty] | 0BT | DG_8-10-55.2_clear | Clear | Stratobel Clearlite | - | 1.2055 | 0.692 | 0.768 | - | _TC
Double Glazing w/ thermal curtain
[10 empty] | 2AT | DG_8¦-18Arg-55.2_ | Sunergy Clear | Stratobel Clearlite | - | 1.0147 | 0.492 | 0.593 | midSHG_midLT | _TC
[10 empty] | 2BT | DG_8¦-18Arg-55.2_ | Planibel top Nplus | Stratobel Clearlite | - | 0.86983 | 0.539 | 0.76 | midSHG_highLT | _TC
[10 empty] | 2CT | DG_8-18Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | - | 0.86441 | 0.592 | 0.768 | highSHG_highLT | _TC
[10 empty] | 2DT | DG_8¦-18Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | - | 0.86259 | 0.341 | 0.696 | lowSHG_highLT | _TC
[10 empty] | 2ET | DG_8¦-18Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | - | 0.85343 | 0.248 | 0.493 | lowSHG_midLT | _TC
[10 empty] | 2FT | DG_8¦-18Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | - | 0.84899 | 0.183 | 0.302 | lowSHG_lowLT | _TC
Triple Glazing w/ thermal curtain
[10 empty] | 3AT | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-72 | Stratobel Clearlite | Planibel Clearvision | 0.70209 | 0.318 | 0.643 | lowSHG_highLT | _TC
[10 empty] | 3BT | TG_8¦-14Arg-6-14Arg-55.2_ | Stopray Vision-51T | Stratobel Clearlite | Planibel Clearvision | 0.69518 | 0.229 | 0.455 | lowSHG_midLT | _TC
[10 empty] | 3CT | TG_8-14Arg-6-14Arg-¦55.2_ | Clearvision | Stratobel Low-e Top N+ | Planibel Clearvision | 0.67549 | 0.554 | 0.709 | highSHG_highLT | _TC
[10 empty] | 3DT | TG_8¦-14Arg-6-14Arg-¦55.2_ | Sunergy Clear | Stratobel Low-e Top N+ | Planibel Clearvision | 0.59962 | 0.374 | 0.523 | midSHG_midLT | _TC
[10 empty] | 3ET | TG_8¦-14Arg-6-14Arg-¦55.2_ | Planibel top Nplus | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.51914 | 0.386 | 0.6 | midSHG_highLT | _TC
[10 empty] | 3FT | TG_8¦-14Arg-6-14Arg-¦55.2_ | Stopray Vision-36T | Stratobel iplus Top 1.0 | Planibel Clearvision | 0.51449 | 0.164 | 0.284 | lowSHG_lowLT | _TC

## Loads
Loads
People
Basement_Density | per floor area | 0 | p/m²
Core_Density | floor area per pers | 2 | m²/p | 1 personne par étage
| fraction radiant | 0.3 | -
Data Center_Density | per floor area | 0 | p/m²
Hall_Density | floor area per pers | 9 | m²/p | Obyn et al.
| fraction radiant | 0.3 | -
Offices_Density | floor area per pers | 8-12 | m²/p | Open space, NBN-EN-13779, 2007, in Obyn et al.
| fraction radiant | 0.3 | - | > Flex office, plus de densité
Light
Offices_Recessed ligting | W per floor area | 5-10 | W/m² | /100 lux = 1-2 W/m². 500 lux for the office space > 8 à 10W/m², but could reach 5 W/m²
Recessed ligting, lighting (relatively low light level) via recessed ceiling luminaires supplemented by desk lamps. The internal load is reduced by the air return through the luminaires. | Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Core_Recessed ligting | W per floor area | 3-6 | W/m²
| Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Basement_Suspended lighting | W per floor area | 3 | W/m²
| Fraction radiant | 0.42 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
DataCenter_Recessed ligting | W per floor area | 0 | W/m²
| Fraction radiant | 0.37 | - | https://designbuilder.co.uk/helpv2/Content/_General_lighting.htm
| Fraction visible | 0.18 | -
| Return air fraction | 0 | -
Equipment
Office_Equipments_Plugs | W per floor area | 150 | W/pers | computer with charger, compact printer… (computer = 100-120 /pers
| Fraction latent | 0 | -
| Fraction radiant | 0.22 | - | https://help.iesve.com/ve2018/table_11_radiant_fraction_for_casual_gains.htm#
| Fraction lost | 0 | -
DataCenter_Plugs | W per floor area | 200 | W/m²
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Core_Equipments_Plug | W per floor area | 2 | W/m² | plusieurs/
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Core_Equipments_Elevators | Design level | 80 | W | ASHRAE 90.1-2010LobbyFor Elevator
| Fraction latent | 0 | -
| Fraction radiant | 0.5 | -
| Fraction lost | 0 | -
Basement_Equipments | W per floor area | 0 | W/m²
| Fraction latent |  | -
| Fraction radiant |  | -
| Fraction lost |  | -
Internal mass
Offices | Surface area | 4 | m²/p
| Construction | Wood furniture
Hall | Surface area | 20 | m²
| Construction | Wood furniture
Core | Surface area | 10 | m²
| Construction | Wood furniture

## Space types
Space types
Design specification outdoor air
Offices | Outdoor air flow per person | 0.0061111 | m³/s.p | https://www.cstc.be/homepage/index.cfm?cat=publications&sub=infofiches&pag=42&art=2&lang=fr#3
Hall | Outdoor air flow per floor area | 0.00325 | m³/s.p | https://www.cstc.be/homepage/index.cfm?cat=publications&sub=infofiches&pag=42&art=2&lang=fr#3
Core | Outdoor air flow per floor area | 0.00072222 | m³/s.p
Data center | Outdoor air flow per floor area | 0.000254 | m/s | ASHRAE 62.1-2007, Office Buildings, Telephone/data entry
Basement | Outdoor air flow per floor area | 0.00031 | m/s

## Facility
Facility
Data
Number of stories | 10
Number of above ground stories | 9
Nominal floor to floor height | 3.7
Nominal floor to ceiling height | 3

## Spaces
Spaces
Shading controls
Exterior shade | Shading device material name | EnviroScreen 810/936, greylight)silver
| Shading control type | On if high zone air temp and high solar on window
| Schedule name | Exterior shading_on
| Setpoint 1 | 22 | °C
| Shading control is scheduled | Yes | -
| Glare control is active | Yes
| Setpoint 2 | 250 | W/m²
| Multiple surface control type | Sequential
Thermal curtain
Frame and divider
Exterior shade

## hvac_VAV
HVAC systems, VAV, basic
Rooftop VAV with reheat #1 |  |  |  |  | > | > | > | Systems
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules
| Use night cycle | Cycle on full system if heating or cooling required | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | deck temperature |  | see schedule
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | no economizer | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | off
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Name | Night cycle 1 |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html | [6 empty] | definition | heat pump used to heat and/or cool a building by exchanging heat with ground, often through a vapor-compression refrigeration cycle. It uses the earth all the time, without any intermittency, as a heat source (in the winter) or a heat sink (in the summer).
| Applicability schedule | always on discrete
| Control type | Cycle on any | [5 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance | 1 | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
| Cycling run time control type | fixed run time
| Cycling run time | 3600 | s
Air loop | Design supply air flow rate | autosized | m³/s
| Design return air flow fraction of supply air flow | 1
Sizing system | Type of load to size on | sensible
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 0.3
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 12.8 | °C
| Central heating design supply air temperature | 12.8 | °C
| Sizing option | NonCoincident
| 100% outdoor air in cooling | yes
| 100% outdoor air in heating | yes
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | Ventilation rate procedure
| Zone maximum outdoor air fraction | 1
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | autosized | -
| Dedicated outdoor air high setpoint temperature for design | autosized | -
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -
Coil heating water | Availability schedule name | Always on, discret | -
| U-factor times area value | autosized | W/K
| Maximum water flow rate | autosized | m³/s
| Performance input method | Ufactor times area and design water flow rate | -
| Rated capacity | autosized | W/K
| Rated inlet water temperature | 82 | °C
| Rated inlet air temperature | 16.5 | °C
| Rated outlet water temperature | 71 | °C
| Rated outlet air temperature | 32 | °C
| Rated ratio for air and water convection | 0.5 | -
Coil cooling water | Availability schedule name | Always on, discret
| Design water flow rate | autosized | m³/s
| Design inlet water temperature | autosized | °C
| Design inlet air temperature | autosized | °C
| Design outlet air temperature | autosized | °C
| Design inlet air humidity ratio | autosized | kgH2O/kgair
| Design outlet humidity ratio | autosized | kgH2O/kgair
| Type of analysis | simple analysis
| Heat exchanger configuration | cross flow
Air Terminal Single Duct VAV Reheat | Availability schedule name | Always on, discret
| Maximum air flow rate | autosized | m³/s
| Zone minimum air flw input method | constant | -
| Constant minimum air flow fraction | 0.3 | -
| Fixed minimum air flow rate | 0 | m³/s
Minimum air flow fraction schedule name
| Reheat coil name | Coil heating water | -
| Maximum hot water or steam flow rate | autosized | m³/s
| Minimum hot water or steam flow rate | 0 | m³/s
| Convergence tolerance | 0.001 | -
| Damper heating action | normal | -
| Maximum flow per zone floor area during reheat | autosized | m/s
| Maximum flow fraction during reheat | autosized | -
| Maximum reheat air temperature | 35 | °C
Fan Variable Volume | Fan total efficiency | 0.6 | -
| Pressure rise | 500 | Pa
| Maximum flow rate | autosized | m³/s
| Fan power minimum flow rate input method | Fixed flow rate
| Fan power minimum fraction | 0
| Fan power minimum air flow rate | 0 | M³/s
| Motor efficiency | 0.93
| Motor in Airstream fraction | 1 | -
| Fan power coefficient 1 | 0.04 | -
| Fan power coefficient 2 | 0.099
| Fan power coefficient 3 | -0.07
| Fan power coefficient 4 | 0.944
Chilled water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 0 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 7.22 | °C
| Loop design temperature difference | 6.67 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Chiller electric, EIR | Reference capacity | autosized | W
| Reference COP | 5.5 | -
| Reference leaving chilled water temperature | 6.7 | °C
| Reference entering condenser fluid temperature | 29.4 | °C
| Reference chilled water flow rate | autosized | m³/s
| Reference condenser fluid flow rate | autosied | m³/s
| Minimum part load ratio | 0.1 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Minimum unloading ratio | 0.2 | -
| Condenser fan power ratio | 0 | -
| Fraction of compressor electric consumption rejected by condenser | 1 | -
| Leavind chilled water lower temperature limit | 2 | °C
Hot water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 0 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 82 | °C
| Loop design temperature difference | 11 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Boiler hot water | Fuel type | Natural gas | -
| Nominal capacity | autosized | W
| Nominal thermal efficiency | 0.8 | -
| Efficiency curve temperature evaluation variable | Leaving boiler | -
| Design water flow rate | autosized | m³/s
| Minimum part load ratio | 0 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Water outlet upper temperature limit | 99 | °C
| Boiler flow mode | constant flow | -
| Parasitic electric load | 0 | W
| Sizing factor | 1
VAV with reheat #2
Data center, sizing | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | khH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | khH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | autosized | -
| Dedicated outdoor air high setpoint temperature for design | autosized | -
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -

## hvac_VAV_optimised
HVAC systems, VAV, optimised
VAV with a high efficiency multizone VAV HVAC system, one per floor. Centralized cooling with zone level heating. |  |  |  |  | > | > | > | Systems
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules
| Use night cycle | Cycle on full system if heating or cooling required | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | controlled by an outdoor air reset setpoint manager |  | see schedule
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | Differential enthalpy | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | on
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Name | Night cycle 1 |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html | [6 empty] | definition | heat pump used to heat and/or cool a building by exchanging heat with ground, often through a vapor-compression refrigeration cycle. It uses the earth all the time, without any intermittency, as a heat source (in the winter) or a heat sink (in the summer).
| Applicability schedule | always on discrete
| Control type | Cycle on any | [5 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance | 1 | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
| Cycling run time control type | fixed run time
| Cycling run time | 3600 | s
Air loop | Design supply air flow rate | autosized | m³/s
| Design return air flow fraction of supply air flow | 1
Sizing system | Type of load to size on | sensible
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 0.3
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 12.8 | °C
| Central heating design supply air temperature | 40 | °C
| Sizing option | NonCoincident
| 100% outdoor air in cooling | No
| 100% outdoor air in heating | No
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | Ventilation rate procedure
| Zone maximum outdoor air fraction | 1
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | autosized | -
| Dedicated outdoor air high setpoint temperature for design | autosized | -
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -
Coil heating water | Availability schedule name | Always on, discret | -
| U-factor times area value | autosized | W/K
| Maximum water flow rate | autosized | m³/s
| Performance input method | Ufactor times area and design water flow rate | -
| Rated capacity | autosized | W/K
| Rated inlet water temperature | 82 | °C
| Rated inlet air temperature | 16.5 | °C
| Rated outlet water temperature | 71 | °C
| Rated outlet air temperature | 32 | °C
| Rated ratio for air and water convection | 0.5 | -
Coil cooling water | Availability schedule name | Always on, discret
| Design water flow rate | autosized | m³/s
| Design inlet water temperature | autosized | °C
| Design inlet air temperature | autosized | °C
| Design outlet air temperature | autosized | °C
| Design inlet air humidity ratio | autosized | kgH2O/kgair
| Design outlet humidity ratio | autosized | kgH2O/kgair
| Type of analysis | simple analysis
| Heat exchanger configuration | cross flow
Air Terminal Single Duct VAV No Reheat | Maximum air flow rate | autosized | m³/s
| Zone minimum air flw input method | constant | -
| Constant minimum air flow fraction | 0.3 | -
| Fixed minimum air flow rate | autosized | m³/s
Minimum air flow fraction schedule name
| Control for outdoor air | No
Fan Variable Volume | Fan total efficiency | 0.69 | -
| Pressure rise | 1125 | Pa
| Maximum flow rate | autosized | m³/s
| Fan power minimum flow rate input method | Fixed flow rate
| Fan power minimum fraction | 0.6
| Fan power minimum air flow rate | 0 | M³/s
| Motor efficiency | 0.9
| Motor in Airstream fraction | 1 | -
| Fan power coefficient 1 | 0.04 | -
| Fan power coefficient 2 | 0.088
| Fan power coefficient 3 | -0.07
| Fan power coefficient 4 | 0.944
Heat Exchanger Air To Air Sensible And Latent
| Nominal supply air flow rate | autosized | m³/s
| Sensible effectiveness at 100% heating air flow | 0.75
| Latent effectiveness at 100% heating air flow | 0.69
| Sensible effectiveness at 75% heating air flow | 0.75
| Latent effectiveness at 75% heating air flow | 0.69
| Sensible effectiveness at 100% cooling air flow | 0.75
| Latent effectiveness at 100% cooling air flow | 0.69
| Sensible effectiveness at 75% cooling air flow | 0.75
| Latent effectiveness at 75% cooling air flow | 0.69
| Nominal electric power | 0 | W
| Supply air outlet temperature control | Yes
| Heat exchanger type | Plate
| Frost control type | Exhaust only
| Threshold temperature | -12.2 | °C
| Initial defrost time fraction | 0.167
| Rate of defrost time fraction increase | 0.024 | /K
| Economizer lockout | No
Chilled water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 98 | °C
| Minimum loop temperature | 1 | °C
| Maximum loop flow rate | autosized | m³/s
| Minimum loop flow rate | 0 | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 6.7 | °C
| Loop design temperature difference | 6.7 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Chiller electric, EIR | Reference capacity | autosized | W
| Reference COP | 2.93 | -
| Reference leaving chilled water temperature | 6.7 | °C
| Reference entering condenser fluid temperature | 29.4 | °C
| Reference chilled water flow rate | autosized | m³/s
| Reference condenser fluid flow rate | autosied | m³/s
| Minimum part load ratio | 0.1 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Minimum unloading ratio | 0.2 | -
| Condenser fan power ratio | 0 | -
| Fraction of compressor electric consumption rejected by condenser | 1 | -
| Leavind chilled water lower temperature limit | 2 | °C
Hot water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 10 | °C
| Maximum loop flow rate | autosized | m³/s
| Minimum loop flow rate | 0 | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 82 | °C
| Loop design temperature difference | 11 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Boiler hot water | Fuel type | Natural gas | -
| Nominal capacity | autosized | W
| Nominal thermal efficiency | 0.9 | -
| Efficiency curve temperature evaluation variable |  | -
| Design water flow rate | autosized | m³/s
| Minimum part load ratio | 0 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Water outlet upper temperature limit | 99 | °C
| Boiler flow mode | constant flow | -
| Parasitic electric load | 0 | W
| Sizing factor | 1

## hvac_VRF
HVAC systems, VRF
VRF, variable refrigerant flow system with multiple indoor units and an outdoor unit |  |  |  |  | > | > | > | Systems
Time of operation | HVAC operation schedule | HVAC_Operation |  | see schedules
| Use night cycle | follow the hvac operation schedule | [5 empty] | - | ASHP | Air source heat pump
[11 empty] | definition | absorbs heat from a colder place and release it into a warmer place using the same vapor-compression refrigeration process and same external heat exchanger with fan as used by an air conditioners. Unlike an air conditioning unit, however, it is able to both warm and cool building
Supply air temperature | Supply air temperature schedule | Temperature setpoint schedule |  | see schedule
[8 empty] | x | EAHP | Exhaust Air Heat Pump
Mechanical ventilation | Economizer | no economizer | [8 empty] | definition | extracts heat from the exhaust air of a building and transfers the heat to the supply air, hot tap water and/or hydronic heating system (underfloor heating, radiators).
| Demand controlled ventilation | on
[8 empty] | x | GSHP | ground source heat pump
Availability managers | Name | none |  | https://bigladdersoftware.com/epx/docs/8-9/input-output-reference/group-system-availability-managers.html | [6 empty] | definition | heat pump used to heat and/or cool a building by exchanging heat with ground, often through a vapor-compression refrigeration cycle. It uses the earth all the time, without any intermittency, as a heat source (in the winter) or a heat sink (in the summer).
Applicability schedule
| Control type | [6 empty] | v | VRF | Variable Refrigerant Flow
| Thermostat tolerance |  | K | [7 empty] | definition | use refrigerant as the cooling and heating medium. This refrigerant is conditioned by a single or multiple condensing units (which may be outdoors or indoors, water or air cooled), and is circulated within the building to multiple indoor units.
Cycling run time control type
| Cycling run time |  | s
DOAS per building story | Design supply air flow rate | autosized | m³/s
| Design return air flow fraction of supply air flow | 1
Sizing system | Type of load to size on | Ventilation requirement
| Design outdoor air flow rate | autosized
| Central heating maximum system air flow ratio | 0.3
| Preheat design temperature | 7 | °C
| Preheat design humidity ratio | 0.008 | kgH2O/kgair
| Precool design temperature | 12.8 | °C
| Precool design humidity ratio | 0.008 | kgH2O/kgair
| Central cooling design supply air temperature | 12.8 | °C
| Central heating design supply air temperature | 40 | °C
| Sizing option | NonCoincident
| 100% outdoor air in cooling | yes
| 100% outdoor air in heating | yes
| Central cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Central heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Cooling design air flow method | design day
| Cooling design air flow rate | 0 | m³/s
| Heating design air flow method | design day
| Heating design air flow rate | 0 | m³/s
| System outdoor air method | Ventilation rate procedure
| Zone maximum outdoor air fraction | 1
Thermal zones sizing: core, offices & hall | Zone cooling design supply air temperature input method | Supply Air Temperature | -
| Zone cooling design supply air temperature | 13 | °C
| Zone cooling design supply air temperature difference | 10 | K
| Zone heating design supply air temperature input method | Supply Air Temperature | -
| Zone heating design supply air temperature | 40 | °C
| Zone heating design supply air temperature difference | 10 | K
| Zone cooling design supply air humidity ratio | 0.0085 | kgH2O/kgair
| Zone heating design supply air humidity ratio | 0.008 | kgH2O/kgair
| Zone heating sizing factor |  | -
| Zone cooling sizing factor |  | -
| Cooling design air flow method | Design day | -
| Cooling design air flow rate | 0 | m³/s
| Cooling minimum air flow per zone floor area | 0.000762 | m/s
| Cooling minimum air flow | 0 | m³/s
| Cooling minimum air flow fraction | 0 | -
| Heating design air flow method | Design day | -
| Heating design air flow rate | 0 | m³/s
| Heating maximum air flow per zone floor area | 0.002 | m/s
| Heating maximum air flow | 0.142 | m³/s
| Heating maximum air flow fraction | 0.3 | -
| Account for dedicated outdoor air system | No | -
| Dedicated outdoor air system control strategy | Neutral supply air | -
| Dedicated outdoor air low setpoint temperature for design | autosized | -
| Dedicated outdoor air high setpoint temperature for design | autosized | -
| Design zone air distribution effectiveness in cooling mode | 1 | -
| Design zone air distribution effectiveness in heating mode | 1 | -
| Design zone secondary recirculation fraction | 0 | -
| Design minimum zone ventilation efficiency | 0.6 | -
Coil Heating DX Single Speed | Rated total heating capacity | autosized | W
| rated COP | 5
| Rated air flow rate | autosized | m³/s
| Unit internal static air pressure | 773.3 | Pa
| Minimum outdoor dry-bulb temperature for compressor operation | -8 | °C
| Maximum outdoor dry-bulb temperature for defrost operation | 5 | °C
Coil Heating DX Single Speed | Availability schedule name | Always on, discret
| Efficiency | 1
| Nominal capacity | autosized
Coil Cooling DX Two Speed | Rated high speed total cooling capacity | autosized | W
| Rated high speed sensible heat ratio | autosized
| Rated high speed COP | 2.93
| Rated high speed air flow rate | autosized | m³/s
| Unit internal static air pressure | 773.3 | Pa
| Rated low speed total cooling capacity | autosized | W
| Rated low speed sensible heating capacity | autosized | W
| Rated low speed COP | 2.93
| Rated low speed air flow rate | autosized | m³/s
| Minimum outdoor dry-bulb temperature for compressor operation | -25 | °C
Air Terminal Single Duct VAV No Reheat | Maximum air flow rate | autosized | m³/s
| Zone minimum air flw input method | constant | -
| Constant minimum air flow fraction | 0 | -
| Fixed minimum air flow rate | autosized | m³/s
Minimum air flow fraction schedule name
| Control for outdoor air | Yes
VRF Terminal Unit | Availability schedule name | Always on, discret
| Supply air flow rate during cooling operation | autosized | m³/s
| Supply air flow rate when no cooling is needed | autosized | m³/s
| Supply air flow rate during heating operation | autosized | m³/s
| Supply air flow rate when no heating is needed | autosized | m³/s
| Outdoor air flow rate during cooling operartion | 0 | m³/s
| Outdoor air flow rate during heating operartion | 0 | m³/s
| Outdoor air flow rate when no cooling or heating is needed | 0 | m³/s
| Supply air fan operating mode schedule | Always off, discret
| Zone terminal unit on parasitic electric energy use | 30 | W
| Zone terminal unit on parasitic electric energy use | 20 | W
| Rated total heating capacity sizing ratio | 1
| Maximum supply air temperature from supplemental heater | autosized | °C
| Maximum outdoor air temperature for supplemental heater | 21 | °C
Fan, Terminal Unit Variable Refrigerant Flow Fan | Availability schedule name | Always on, discret
| Fan total efficiency | 0.6
| Pressure rise | 299 | Pa
| Maximum flow rate | autosized
| Motor efficiency | 0.85
| Motor in airstream fraction | 1
Coil, Terminal Unit Variable Refrigerant Flow Cooling Coil | Availability schedule name | Always on, discret
| Rated total cooling capacity | autosized
| Rated sensible heat ratio | autosized
| Rated air flow rate | autosized
Fan Variable Volume | Fan total efficiency | 0.6 | -
| Pressure rise | 1120 | Pa
| Maximum flow rate | autosized | m³/s
| Fan power minimum flow rate input method | Fixed flow rate
| Fan power minimum fraction | 0.6
| Fan power minimum air flow rate | 0 | m³/s
| Motor efficiency | 0.85
| Motor in Airstream fraction | 1 | -
| Fan power coefficient 1 | 0.04 | -
| Fan power coefficient 2 | 0.088
| Fan power coefficient 3 | -0.07
| Fan power coefficient 4 | 0.944
Heat Exchanger Air To Air Sensible And Latent
| Nominal supply air flow rate | autosized | m³/s
| Sensible effectiveness at 100% heating air flow | 0.76
| Latent effectiveness at 100% heating air flow | 0.68
| Sensible effectiveness at 75% heating air flow | 0.81
| Latent effectiveness at 75% heating air flow | 0.73
| Sensible effectiveness at 100% cooling air flow | 0.76
| Latent effectiveness at 100% cooling air flow | 0.68
| Sensible effectiveness at 75% cooling air flow | 0.81
| Latent effectiveness at 75% cooling air flow | 0.73
| Nominal electric power | 0 | W
| Supply air outlet temperature control | Yes
| Heat exchanger type | Plate
| Frost control type | Exhaust only
| Threshold temperature | 10 | °C
| Initial defrost time fraction | 0.167
| Rate of defrost time fraction increase | 0.013 | /K
| Economizer lockout | Yes
Chilled water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 0 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 7.22 | °C
| Loop design temperature difference | 6.67 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Chiller electric, EIR | Reference capacity | autosized | W
| Reference COP | 5.5 | -
| Reference leaving chilled water temperature | 6.7 | °C
| Reference entering condenser fluid temperature | 29.4 | °C
| Reference chilled water flow rate | autosized | m³/s
| Reference condenser fluid flow rate | autosied | m³/s
| Minimum part load ratio | 0.1 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Minimum unloading ratio | 0.2 | -
| Condenser fan power ratio | 0 | -
| Fraction of compressor electric consumption rejected by condenser | 1 | -
| Leavind chilled water lower temperature limit | 2 | °C
Hot water loop |  |  |  |  | > | > | >
Plant loop | fluid type | water
| Maximum loop temperature | 100 | °C
| Minimum loop temperature | 0 | °C
| Maximum loop flow rate | autosized | m³/s
| Plant loop volume | autocalculate | m³/s
| Load distribution sheme | optimal
Sizing | Design loop exit temperature | 82 | °C
| Loop design temperature difference | 11 | K
| Sizing option | Non coincident
| Zone timesteps in averaging window | 1
Boiler hot water | Fuel type | Natural gas | -
| Nominal capacity | autosized | W
| Nominal thermal efficiency | 0.8 | -
| Efficiency curve temperature evaluation variable | Leaving boiler | -
| Design water flow rate | autosized | m³/s
| Minimum part load ratio | 0 | -
| Maximum part load ratio | 1 | -
| Optimum part load ratio | 1 | -
| Water outlet upper temperature limit | 99 | °C
| Boiler flow mode | constant flow | -
| Parasitic electric load | 0 | W
| Sizing factor | 1

## Thermal zones
Thermal zones
Cooling sizing parameters
For each zone | zone cooling design supply air temperature | 13 | °C
| zone cooling design supply air humidity ratio | 0.0085
zone cooling sizing factor
| cooling minimum air flow per zone floor area | 0.000762 | m³/s.m²
| Design zone air deistribution effectiveness in cooling mode | 1
| Cooling minimum air flow fraction | 0
| Cooling design air flow method | Design day
| Cooling design air flow rate | 0 | m³/s.m²
| Cooling minimum air flow | 0 | m³/s.m²
Heating sizing parameters
For each zone | zone heating design supply air temperature | 40 | °C
| zone heating design supply air humidity ratio | 0.008
zone heating sizing factor
| Heating maximum air flow per zone floor area | 0.002032 | m³/s.m²
| Design zone air distribution effectiveness in heating mode | 1
| Heating maximum air flow fraction | 0.3
| Heating design air flow method | Design day
| Heating design air flow rate | 0 | m³/s.m²
| Heating maximum air flow | 0.14158 | m³/s.m²

## Output Variables
Energy Plus, Output Variables
Weather
Site Outdoor Air Drybulb Temperature | Hourly
Equipment
Electric Equipment Electric Energy | Hourly
Lighting
Lights Electric Energy | Hourly
Zone Lights Electric Energy | Hourly
Internal gain
Zone Total Internal Total Heating Energy | Hourly
Comfort
Zone Air Temperature
Zone Mean Air Temperature | Hourly
Zone Mean Radiant Temperature | Hourly
Zone Operative Temperature | Hourly
Zone Thermal Comfort CEN 15251 Adaptive Model Temperature | Hourly
Ventilation
Zone Ventilation Fan Electric Energy | Hourly
Windows
Zone Windows Total Heat Gain Energy | Hourly
Zone Windows Total Heat Loss Energy | Hourly
Zone Windows Total Transmitted Solar Radiation Rate | Hourly
Zone Windows Total Transmitted Solar Radiation Energy | Hourly

## Simulations
Scenario analysis, glazing types
48 | 3 steps, 16 runs each
| step | 1 | 2 | 3
| name | glazing type | ext shading | thermal curtain
| number of simulations | 16 | 16 | 16
| exterior shading | no | yes | yes
| interior thermal curtain | no | no | yes
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| electricity grid | BE
| density, offices | 10 m²/p.
| lighting power | 8 W/m²
| types of glazing | 16, which are:
init: old double glazing, bronze
double glazing, clear, air
single glazing
single glazing, coated
double glazing, coated, 6 types
triple glazing, coated, 6 types
Scenario analysis, glass-to-wall ratio
8 | 1 steps, 8 runs
| step | 4
| name | glazing type
| number of simulations | 8
| glass-to-wall ratio | 80% of the width
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| electricity grid | BE
| density, offices | 10 m²/p.
| lighting power | 8 W/m²
| exterior shading | yes
| interior thermal curtain | no
| types of glazing | 8, which are:
init: old double glazing, bronze
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types
Scenario analysis, high-tech
6 | 6 steps, 1 run each
| step | 5 | 6 | 7 | 8 | 9 | 10
| name | krypton, dg | krypton, tg | xenon, tg | CCF | vaccum | smart
| number of simulations | 1 | 1 | 1 | 1 | 1 | 1
| types of glazing | double glazing, krypton | triple glazing, krypton | triple glazing, xenon | closed cavity facade | vaccum glazing | smart double glazing
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| electricity grid | BE
| density, offices | 10 m²/p.
| lighting power | 8 W/m²
| exterior shading | no
| interior thermal curtain | no
Sensitivity analysis, setpoint temperature
16 | 2 steps, 8 runs each
| step | 11 | 12
| name | americanisation | sufficiency
| number of simulations | 8 | 8
| cooling setpoint | 24 | 27
| heating setpoint | 21 | 18
| exterior shading | yes | yes
| interior thermal curtain | no | yes
main parameters
| HVAC | VAV, basic
| electricity grid | BE
| density, offices | 10 m²/p.
| lighting power | 8 W/m²
| types of glazing | 8, which are:
init: old double glazing, bronze
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types
Sensitivity analysis, internal gains
16 | 2 steps, 8 runs each
| step | 13 | 14
| name | density_8 | density_12
| number of simulations | 8 | 8
| lighting power | 10 W/m² | 5 W/m²
| density, offices | 8 m²/p. | 12 m²/p.
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| electricity grid | BE
| exterior shading | yes
| interior thermal curtain | no
| types of glazing | 8, which are:
init: old double glazing, bronze
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types
Sensitivity analysis, hvac system
48 | 6 steps, 8 runs each | [6 empty] | Energy mix
| step | 15 | 16 | 17 | 18 | 19 | 20 | Lifespan
| name | VAV+, 26-19 | VAV+, 24-21 | VAV+, 27-18 | VRF, 26-19 | VRF, 24-21 | VRF, 27-18
| number of simulations | 8 | 8 | 8 | 8 | 8 | 8 | HVAC
| HVAC | VAV, efficient | VAV, efficient | VAV, efficient | VRF | VRF | VRF
| exterior shading | yes | yes | yes | yes | yes | yes | 3 | electrification | heat pumps | rooftop
| interior thermal curtain | no | no | yes | no | no | yes |  |  | heating heat pump | direct expansion single speed | https://www.ehpa.org/
| cooling setpoint | 26 | 24 | 27 | 26 | 24 | 27 |  |  | cooling heat pump | direct expansion single speed / chilled ceiling
| heating setpoint | 19 | 21 | 18 | 19 | 21 | 18 | 2 | VAV, upgraded | VAV with reheat | rooftop
[10 empty] | heat recovery boiler | recovery efficiency: 80%
main parameters
| electricity grid | BE
| density, offices | 10 m²/p. | [7 empty] | electric chiller | refrigerating machine + cop + contorl deck temperature
| lighting power | 8 W/m² | [5 empty] | 1 | VAV, current | VAV with reheat | rooftop
| types of glazing | 8, which are: | [7 empty] | heat recovery boiler | recovery efficiency: 50%
|  | init: old double glazing, bronze | [7 empty] | electric chiller | refrigerating machine | Deck temperature
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types
Sensitivity analysis, energy mix for electricity from grid
LCA ONLY
40 | 5 steps, 8 runs each
| step | 21 | 22 | 23 | 24 | 25
| name | NL | DE | PL | FR | CH
| number of simulations | 8 | 8 | 8 | 8 | 8
| electricity grid | Netherlands | Germany | Poland | France | Switzerland
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| lighting power | 8 W/m²
| density, offices | 10 m²/p.
| exterior shading | yes
| interior thermal curtain | no
| types of glazing | 8, which are:
init: old double glazing, bronze
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types
Sensitivity analysis, climate change
8 | 1 step, 8 runs each
| step | 26
| name | climate change
| number of simulations | 8
| weather data | tbc
main parameters
| cooling setpoint | 26
| heating setpoint | 19
| HVAC | VAV, basic
| electricity grid | BE
| lighting power | 8 W/m²
| density, offices | 10 m²/p.
| exterior shading | yes
| interior thermal curtain | no
| types of glazing | 8, which are:
init: old double glazing, bronze
double glazing, clear, air
double glazing, coated, 3 types
triple glazing, coated, 3 types